## Sheet1
BESTEST OUTPUT FORM FOR FUEL-FIRED FURNACE TEST CASES HE100-HE170 and HE210-HE230 (equivalent of Std140_HE_Output.xls, same cells B20.. B97)
Software: Pinocchio-EP (Studio HVAC) on EnergyPlus 26.1.0-6f2e40d102; generated by tools/std140/he/report.py
HE210-HE230 weather: official HE210W.WY2 (Std 140-2023 accompanying files), converted to EPW by weather.mjs wy2ToEpw
TOTAL FURNACE LOAD
CODENAME: | Pinocchio-EP
COUNTRY: | India
GJ
CASE HE100 | 77.76
CASE HE110 | 77.76
CASE HE120 | 31.2691
CASE HE130 | 0.0085064
CASE HE140 | 31.269
CASE HE150 | 29.7651
CASE HE160 | 30.6532
CASE HE170 | 29.7651
CASE HE210 | 42.2647
CASE HE220 | 40.0333
CASE HE230 | 34.587
TOTAL FURNACE INPUT
CODENAME: | Pinocchio-EP
COUNTRY: | India
GJ
CASE HE100 | 77.7561
CASE HE110 | 97.1951
CASE HE120 | 38.4914
CASE HE130 | 0.01519
CASE HE140 | 39.0788
CASE HE150 | 37.157
CASE HE160 | 38.296
CASE HE170 | 37.157
CASE HE210 | 52.6935
CASE HE220 | 49.833
CASE HE230 | 43.3054
FUEL CONSUMPTION
CODENAME: | Pinocchio-EP
COUNTRY: | India
m3/s
CASE HE100 | 0.00026314
CASE HE110 | 0.00032893
CASE HE120 | 0.00013026
CASE HE130 | 5.1407e-08
CASE HE140 | 0.00013225
CASE HE150 | 0.00012575
CASE HE160 | 0.0001296
CASE HE170 | 0.00012575
CASE HE210 | 0.00017833
CASE HE220 | 0.00016865
CASE HE230 | 0.00014656
FAN ENERGY (BOTH FANS)
CODENAME: | Pinocchio-EP
COUNTRY: | India
kWh
CASE HE150 | 432
CASE HE160 | 171.1576
CASE HE170 | 473.2855
CASE HE210 | 293.8684
CASE HE220 | 278.1898
CASE HE230 | 481.251
MEAN ZONE TEMPERATURE
CODENAME: | Pinocchio-EP
COUNTRY: | India
C
CASE HE210 | 20.0002
CASE HE220 | 18.5371
CASE HE230 | 15.4003
MAXIMUM ZONE TEMPERATURE
CODENAME: | Pinocchio-EP
COUNTRY: | India
C
CASE HE210 | 20.0009
CASE HE220 | 20.0009
CASE HE230 | 20.0009
MINIMUM ZONE TEMPERATURE
CODENAME: | Pinocchio-EP
COUNTRY: | India
C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 1.8746

## A3-8 ranges
Range case | Quantity | Pinocchio-EP | Lower | Upper | In range
HE210 | totalFurnaceInput_GJ | 52.6935 | 49.86 | 55.11 | YES
HE210 | fanEnergy_kWh | 293.8684 | 279.55 | 308.98 | YES
HE220-HE210 | totalFurnaceInput_GJ | -2.8604 | -5.48 | -0.23 | YES
HE220-HE210 | fanEnergy_kWh | -15.6787 | -30.21 | -0.78 | YES
HE230-HE220 | totalFurnaceInput_GJ | -6.5277 | -9.1 | -3.86 | YES
HE230-HE220 | fanEnergy_kWh | 203.0612 | 186.29 | 216.78 | YES
6 of 6 in range; 5 needed -> PASS

## vs examples (informative)
Quantity | Case | Pinocchio-EP | Analytical/QAS | Example min | Example max | EnergyPlus 1.0.2 (GARD) | Timestep 1/h | GUI cubic PLF
totalFurnaceLoad_GJ | HE100 | 77.76 | 77.74 | 77.75 | 77.94 | 77.75 | 77.76 | 77.76
totalFurnaceLoad_GJ | HE110 | 77.76 | 77.74 | 77.75 | 77.94 | 77.75 | 77.76 | 77.76
totalFurnaceLoad_GJ | HE120 | 31.2691 | 31.1 | 31.1 | 31.25 | 31.1 | 31.2691 | 31.2691
totalFurnaceLoad_GJ | HE130 | 0.0085064 | 0 | 0 | 0.155 | 0 | 0.0068577 | 0.0085064
totalFurnaceLoad_GJ | HE140 | 31.269 | 31.1 | 31.1 | 31.26 | 31.1 | 31.2689 | 31.269
totalFurnaceLoad_GJ | HE150 | 29.7651 | 29.65 | 29.565 | 29.88 | 29.59 | 29.7448 | 29.7651
totalFurnaceLoad_GJ | HE160 | 30.6532 | 31.1 | 30.46 | 31.26 | 30.46 | 30.6531 | 30.6488
totalFurnaceLoad_GJ | HE170 | 29.7651 | 29.65 | 29.565 | 29.88 | 29.59 | 29.7448 | 29.7651
totalFurnaceLoad_GJ | HE210 | 42.2647 |  | 41.36 | 42.057 | 42.04 | 42.2642 | 42.2614
totalFurnaceLoad_GJ | HE220 | 40.0333 |  | 39.41 | 39.87 | 39.87 | 40.046 | 40.0306
totalFurnaceLoad_GJ | HE230 | 34.587 |  | 34.32 | 34.59 | 34.59 | 34.3865 | 34.5833
totalFurnaceInput_GJ | HE100 | 77.7561 | 77.7133 | 77.7133 | 78.417 | 77.7133 | 77.7561 | 75.2121
totalFurnaceInput_GJ | HE110 | 97.1951 | 97.2156 | 96.9201 | 98.02 | 97.2156 | 97.1951 | 94.0151
totalFurnaceInput_GJ | HE120 | 38.4914 | 38.2657 | 38.2657 | 38.556 | 38.2657 | 38.4913 | 37.6478
totalFurnaceInput_GJ | HE130 | 0.01519 | 0 | 0 | 0.142 | 0 | 0.012246 | 0.012334
totalFurnaceInput_GJ | HE140 | 39.0788 | 39.0044 | 38.764 | 39.0044 | 39.0044 | 39.0838 | 39.3208
totalFurnaceInput_GJ | HE150 | 37.157 | 37.0246 | 36.82 | 37.2315 | 36.936 | 37.1449 | 37.3687
totalFurnaceInput_GJ | HE160 | 38.296 | 38.0884 | 37.962 | 38.118 | 38.118 | 38.3006 | 38.5023
totalFurnaceInput_GJ | HE170 | 37.157 | 37.0246 | 36.82 | 37.2315 | 36.936 | 37.1449 | 37.3687
totalFurnaceInput_GJ | HE210 | 52.6935 |  | 50.5284 | 52.371 | 52.0059 | 52.6929 | 52.5087
totalFurnaceInput_GJ | HE220 | 49.833 |  | 47.8691 | 49.466 | 49.3465 | 49.8643 | 49.5451
totalFurnaceInput_GJ | HE230 | 43.3054 |  | 41.3683 | 43.219 | 42.5503 | 43.038 | 42.5463
fanEnergy_kWh | HE150 | 432 | 432 | 432 | 433.3 | 433.3 | 432 | 432
fanEnergy_kWh | HE160 | 171.1576 | 172.76 | 170.2 | 172.385 | 172.2 | 171.1738 | 172.6208
fanEnergy_kWh | HE170 | 473.2855 | 473.18 | 473.1 | 473.4 | 473.1 | 473.2721 | 473.5207
fanEnergy_kWh | HE210 | 293.8684 |  | 281.6 | 298.918 | 291.4 | 293.8654 | 294.7723
fanEnergy_kWh | HE220 | 278.1898 |  | 268.3 | 281.157 | 276.1 | 278.3073 | 278.7406
fanEnergy_kWh | HE230 | 481.251 |  | 431.4 | 478.408 | 431.4 | 478.2959 | 480.8014
tmean | HE210 | 20.0002 |  | 19.98 | 20.01 | 20 | 20.0002
tmean | HE220 | 18.5371 |  | 18.53 | 18.75 | 18.53 | 18.5226
tmean | HE230 | 15.4003 |  | 15.17 | 15.64 | 15.17 | 15.2414
tmax | HE210 | 20.0009 |  | 20 | 21.45 | 20 | 20.0011
tmax | HE220 | 20.0009 |  | 20 | 22.7 | 20 | 20.0011
tmax | HE230 | 20.0009 |  | 20 | 20.14 | 20 | 20.0011
tmin | HE210 | 20 |  | 19.89 | 20 | 20 | 20
tmin | HE220 | 15 |  | 14.94 | 15 | 15 | 15
tmin | HE230 | 1.8746 |  | 1.45 | 4.48 | 4.48 | 2.721