## A
Std140_AE_Output.xlsx
Output Spreadsheet for Standard 140 Airside HVAC Equipment Performance Analytical Verification Cases AE101 through AE445
INSTRUCTIONS
1. Use specified units.
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| C61...J63: | Coil Loads, Fan Coil Air System, AE100 Series Cases
| S61...Y75: | Detailed Outputs, Fan Coil Air System, AE100 Series Cases
| C89...J95: | Coil Loads, Single Zone Air System, AE200 Series Cases
| S89...Z123: | Detailed Outputs, Single Zone Air System, AE200 Series Cases
| C137...O143: | Coil Loads, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| S137...AC171: | Detailed Outputs, Constant Volume Terminal Reheat Air System, AE300 Series Cases
| C185...O191: | Coil Loads, Variable Air Volume Air System, AE400 Series Cases
| S185...AC219: | Detailed Outputs, Variable Air Volume Air System, AE400 Series Cases
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section 6.5
| Software: | Pinocchio-EP (Studio HVAC) / EnergyPlus 26.1.0-6f2e40d102
| Version: | ashrae140-compliance working tree
| Date: | 2026-10-27
Last Hour of Simulation - Summary Outputs - Fan Coil Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Fan Coil Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Air
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (ra)
| AE101 | 2.931 | 0 | 0.5861 | 8.4538 | 0 | 0 | 0 | 6.5151 | [5 empty] | AE101 | Dry bulb temperature (°C) | -29 | 4.4563 | 29.053 | 29.053 | 29.6391 | 21.1219 | 29.6391
| AE103 | 0 | 1.465 | 0.5861 | 0 | 0.76279 | 0 | 0.76279 | 45.6407 | [6 empty] | Humidity ratio (g/gda) | 0.000259 | 0.001612 | 0.001612 | 0.001612 | 0.001612 | 0.002289 | 0.001612
| AE104 | 0 | 2.931 | 0.5861 | 0 | 3.4991 | 2.1836 | 5.6827 | 99.3275 | [6 empty] | Specific volume (L/kgda) | 691.9367 | 788.4649 | 858.3251 | 858.3251 | 859.9899 | 836.7059 | 859.9899
[16 empty] | Enthalpy (J/gda) | -28.5067 | 8.523 | 33.3124 | 33.3124 | 33.9032 | 27.0378 | 33.9032
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
[15 empty] | AE103 | Dry bulb temperature (°C) | 15.5 | 20.7249 | 20.7249 | 18.5234 | 19.1048 | 23.3276 | 19.1048
[16 empty] | Humidity ratio (g/gda) | 0.004684 | 0.006035 | 0.006035 | 0.006035 | 0.006035 | 0.00671 | 0.006035
[16 empty] | Specific volume (L/kgda) | 823.8699 | 840.5912 | 840.5912 | 834.2943 | 835.9573 | 848.9482 | 835.9573
[16 empty] | Enthalpy (J/gda) | 27.4234 | 36.1498 | 36.1498 | 33.9131 | 34.5038 | 40.513 | 34.5038
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
[15 empty] | AE104 | Dry bulb temperature (°C) | 26.9 | 24.8923 | 24.8923 | 14.9219 | 15.4986 | 23.8783 | 15.4986
[16 empty] | Humidity ratio (g/gda) | 0.016767 | 0.013053 | 0.013053 | 0.010521 | 0.010521 | 0.011197 | 0.010521
[16 empty] | Specific volume (L/kgda) | 872.9227 | 862.04 | 862.04 | 829.8798 | 831.5411 | 856.595 | 831.5411
[16 empty] | Enthalpy (J/gda) | 69.8027 | 58.2627 | 58.2627 | 41.5991 | 42.1899 | 52.4927 | 42.1899
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Single Zone Air System
|  | Zone | Zone | Zone | Heating | Cooling Coil | [8 empty] | Last Hour of Simulation - Detailed Outputs - Single Zone Air System
|  | Sensible | Sensible | Latent | Coil | Loads |  |  | Outlet | [7 empty] | Location
| Cases | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | [7 empty] | Outdoor | Mixed | Heat Coil | Cool Coil | Supply | Zone | Return Fan | Return Fan
|  | (QZHsensible) | (QZClatent) | (QZlatent) | (QH) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | [7 empty] | Air | Air | Outlet | Outlet | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | [5 empty] | Cases | Variable | (oa) | (ma) | (hco) | (cco) | (sa) | (z1) | (rfi) | (rfo)
| AE201 | 2.931 | 0 | 0.5861 | 8.3866 | 0 | 0 | 0 | 6.5151 | [5 empty] | AE201 | Dry bulb temperature (°C) | -29 | 4.6517 | 29.053 | 29.053 | 29.6391 | 21.1219 | 21.1219 | 21.4146
| AE203 | 0 | 1.465 | 0.5861 | 0 | 0.82994 | 0 | 0.82994 | 45.6407 | [6 empty] | Humidity ratio (g/gda) | 0.000259 | 0.001612 | 0.001612 | 0.001612 | 0.001612 | 0.002289 | 0.002289 | 0.002289
| AE204 | 0 | 2.931 | 0.5861 | 0 | 3.5663 | 2.1842 | 5.7504 | 99.3081 | [6 empty] | Specific volume (L/kgda) | 691.9367 | 789.0199 | 858.3251 | 858.3251 | 859.9899 | 836.7059 | 836.7059 | 837.5381
| AE205 | 0 | 1.465 | 0.5861 | 0 | 1.9129 | 0 | 1.9129 | 44.1191 | [6 empty] | Enthalpy (J/gda) | -28.5067 | 8.7199 | 33.3124 | 33.3124 | 33.9032 | 27.0378 | 27.0378 | 27.3332
| AE206 | 0 | 1.465 | 0.5861 | 0 | 1.6969 | 1.0228 | 2.7196 | 99.51 | [6 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
| AE226 | 0 | 1.465 | 0.5861 | 0 | 1.5556 | 1.8734 | 3.4291 | 99.7332 | [5 empty] | AE203 | Dry bulb temperature (°C) | 15.5 | 20.9187 | 20.9187 | 18.5234 | 19.1048 | 23.3276 | 23.3276 | 23.618
| AE245 | 0 | 1.465 | 0.5861 | 0 | 2.2079 | 0 | 2.2079 | 33.9953 | [6 empty] | Humidity ratio (g/gda) | 0.004684 | 0.006035 | 0.006035 | 0.006035 | 0.006035 | 0.00671 | 0.00671 | 0.00671
[16 empty] | Specific volume (L/kgda) | 823.8699 | 841.1455 | 841.1455 | 834.2943 | 835.9573 | 848.9482 | 848.9482 | 849.7796
[16 empty] | Enthalpy (J/gda) | 27.4234 | 36.3467 | 36.3467 | 33.9131 | 34.5038 | 40.513 | 40.513 | 40.8084
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
[15 empty] | AE204 | Dry bulb temperature (°C) | 26.9 | 25.0837 | 25.0837 | 14.9219 | 15.4986 | 23.8783 | 23.8783 | 24.1663
[16 empty] | Humidity ratio (g/gda) | 0.016767 | 0.013052 | 0.013052 | 0.010519 | 0.010519 | 0.011194 | 0.011194 | 0.011194
[16 empty] | Specific volume (L/kgda) | 872.9227 | 862.5915 | 862.5915 | 829.8769 | 831.5381 | 856.5921 | 856.5921 | 857.4226
[16 empty] | Enthalpy (J/gda) | 69.8027 | 58.456 | 58.456 | 41.5937 | 42.1844 | 52.4873 | 52.4873 | 52.7826
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
[15 empty] | AE205 | Dry bulb temperature (°C) | 24.9 | 24.0443 | 24.0443 | 18.5216 | 19.1032 | 23.3276 | 23.3276 | 23.618
[16 empty] | Humidity ratio (g/gda) | 0.00448 | 0.005831 | 0.005831 | 0.005831 | 0.005831 | 0.006506 | 0.006506 | 0.006506
[16 empty] | Specific volume (L/kgda) | 850.423 | 849.8102 | 849.8102 | 834.0184 | 835.6815 | 848.6729 | 848.6729 | 849.5043
[16 empty] | Enthalpy (J/gda) | 36.4318 | 39.0039 | 39.0039 | 33.3946 | 33.9854 | 39.9946 | 39.9946 | 40.29
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
[15 empty] | AE206 | Dry bulb temperature (°C) | 23 | 23.4091 | 23.4091 | 18.587 | 19.1607 | 23.3277 | 23.3277 | 23.6142
[16 empty] | Humidity ratio (g/gda) | 0.015561 | 0.014547 | 0.014547 | 0.013364 | 0.013364 | 0.014039 | 0.014039 | 0.014039
[16 empty] | Specific volume (L/kgda) | 859.9499 | 859.7672 | 859.7672 | 844.2155 | 845.8757 | 858.8461 | 858.8461 | 859.676
[16 empty] | Enthalpy (J/gda) | 62.6948 | 60.5359 | 60.5359 | 52.561 | 53.1518 | 59.1611 | 59.1611 | 59.4564
[16 empty] | Mass flow rate (kgda/s) | 0.11367 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
[15 empty] | AE226 | Dry bulb temperature (°C) | 23 | 23 | 23 | 18.5873 | 19.161 | 23.3277 | 23.3277 | 23.6142
[16 empty] | Humidity ratio (g/gda) | 0.015561 | 0.015561 | 0.015561 | 0.013395 | 0.013395 | 0.01407 | 0.01407 | 0.01407
[16 empty] | Specific volume (L/kgda) | 859.9499 | 859.9499 | 859.9499 | 844.2574 | 845.9175 | 858.8878 | 858.8878 | 859.7178
[16 empty] | Enthalpy (J/gda) | 62.6948 | 62.6948 | 62.6948 | 52.6396 | 53.2303 | 59.2396 | 59.2396 | 59.535
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
[15 empty] | AE245 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 18.5098 | 19.0928 | 23.3276 | 23.3276 | 23.6188
[16 empty] | Humidity ratio (g/gda) | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.005155 | 0.005155 | 0.005155
[16 empty] | Specific volume (L/kgda) | 850.423 | 850.423 | 850.423 | 832.1897 | 833.8534 | 846.8487 | 846.8487 | 847.6804
[16 empty] | Enthalpy (J/gda) | 36.4318 | 36.4318 | 36.4318 | 29.9574 | 30.5481 | 36.5573 | 36.5573 | 36.8527
[16 empty] | Mass flow rate (kgda/s) | 0.34102 | 0.34102 | 0.34102 | 0.34102 | 0.34102 | n/a* | 0.34102 | 0.34102
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Constant Volume Terminal Reheat Air System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Constant Volume Terminal Reheat Air System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE301 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 3.5498 | 0 | 0 | 0 | 24.0842 | 7.5089 | 8.1361 | AE301 | Dry bulb temperature (°C) | -29 | 2.4522 | 7.22 | 7.22 | 7.8063 | 29.6578 | 28.1011 | 21.1389 | 22.261 | 21.7432 | 22.0359
| AE303 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 6.517 | 0 | 6.517 | 67.3398 | 2.1955 | 2.3775 |  | Humidity ratio (g/gda) | 0.000259 | 0.001507 | 0.001507 | 0.001507 | 0.001507 | 0.001507 | 0.001507 | 0.002184 | 0.002377 | 0.002288 | 0.002288
| AE304 | 0 | 2.931 | 0.5861 | 0 | 3.517 | 0.8792 | 0 | 10.177 | 6.6159 | 16.7929 | 99.3241 | 0.94249 | 1.4561 |  | Specific volume (L/kgda) | 691.9367 | 782.6415 | 796.1809 | 796.1809 | 797.8457 | 859.8987 | 855.4778 | 836.6141 | 840.0632 | 838.4713 | 839.3036
| AE305 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.2213 | 0 | 9.2213 | 65.048 | 2.1942 | 2.3757 |  | Enthalpy (J/gda) | -28.5067 | 6.241 | 11.0452 | 11.0452 | 11.636 | 33.6545 | 32.0859 | 26.7892 | 28.4111 | 27.6625 | 27.9579
| AE306 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.7655 | 5.7475 | 14.5129 | 99.3849 | 2.2147 | 2.4022 |  | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
| AE326 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 8.2481 | 12.5206 | 20.7687 | 99.9742 | 2.2151 | 2.4027 | AE303 | Dry bulb temperature (°C) | 15.5 | 20.881 | 20.881 | 12.1985 | 12.78 | 19.1176 | 18.6625 | 23.3411 | 24.4554 | 23.9412 | 24.2315
| AE345 | 0 | 1.465 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 9.5096 | 0 | 9.5096 | 50.9943 | 2.1858 | 2.365 |  | Humidity ratio (g/gda) | 0.004684 | 0.00593 | 0.00593 | 0.00593 | 0.00593 | 0.00593 | 0.00593 | 0.006606 | 0.006798 | 0.006709 | 0.006709
[16 empty] | Specific volume (L/kgda) | 823.8699 | 840.8978 | 840.8978 | 816.0669 | 817.73 | 835.8546 | 834.5532 | 848.8458 | 852.2966 | 850.7039 | 851.5353
[16 empty] | Enthalpy (J/gda) | 27.4234 | 36.0431 | 36.0431 | 27.223 | 27.8137 | 34.2518 | 33.7895 | 40.261 | 41.8841 | 41.135 | 41.4303
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
[15 empty] | AE304 | Dry bulb temperature (°C) | 26.9 | 25.6028 | 25.6028 | 12.2015 | 12.78 | 15.4863 | 16.364 | 23.8925 | 25.0069 | 24.4927 | 24.7815
[16 empty] | Humidity ratio (g/gda) | 0.016767 | 0.012336 | 0.012336 | 0.008788 | 0.008788 | 0.008788 | 0.008788 | 0.009463 | 0.009656 | 0.009567 | 0.009567
[16 empty] | Specific volume (L/kgda) | 872.9227 | 863.1192 | 863.1192 | 819.7902 | 821.4521 | 829.2273 | 831.7488 | 854.291 | 857.7573 | 856.1575 | 856.9883
[16 empty] | Enthalpy (J/gda) | 69.8027 | 57.1663 | 57.1663 | 34.4388 | 35.0296 | 37.7933 | 38.6895 | 48.0961 | 49.7253 | 48.9733 | 49.2687
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
[15 empty] | AE305 | Dry bulb temperature (°C) | 24.9 | 24.4881 | 24.4881 | 12.1984 | 12.7801 | 19.116 | 18.6603 | 23.3411 | 24.4554 | 23.9412 | 24.2316
[16 empty] | Humidity ratio (g/gda) | 0.00448 | 0.005726 | 0.005726 | 0.005726 | 0.005726 | 0.005726 | 0.005726 | 0.006402 | 0.006594 | 0.006505 | 0.006505
[16 empty] | Specific volume (L/kgda) | 850.423 | 850.9376 | 850.9376 | 815.8016 | 817.4648 | 835.5789 | 834.2762 | 848.5707 | 852.0204 | 850.4282 | 851.2596
[16 empty] | Enthalpy (J/gda) | 36.4318 | 39.1887 | 39.1887 | 26.7086 | 27.2994 | 33.7334 | 33.2707 | 39.7426 | 41.3653 | 40.6163 | 40.9117
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
[15 empty] | AE306 | Dry bulb temperature (°C) | 23 | 23.7538 | 23.7538 | 12.2016 | 12.78 | 19.1396 | 18.6927 | 23.3412 | 24.4554 | 23.9412 | 24.2301
[16 empty] | Humidity ratio (g/gda) | 0.015561 | 0.011876 | 0.011876 | 0.008794 | 0.008794 | 0.008794 | 0.008794 | 0.009469 | 0.009662 | 0.009573 | 0.009573
[16 empty] | Specific volume (L/kgda) | 859.9499 | 857.1549 | 857.1549 | 819.7976 | 821.4595 | 839.7301 | 838.4463 | 852.7132 | 856.1786 | 854.5792 | 855.41
[16 empty] | Enthalpy (J/gda) | 62.6948 | 54.0946 | 54.0946 | 34.4528 | 35.0436 | 41.5378 | 41.0815 | 47.5471 | 49.1761 | 48.4243 | 48.7196
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
[15 empty] | AE326 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.2016 | 12.7801 | 19.14 | 18.6933 | 23.3412 | 24.4554 | 23.9412 | 24.23
[16 empty] | Humidity ratio (g/gda) | 0.015561 | 0.015561 | 0.015561 | 0.008847 | 0.008847 | 0.008847 | 0.008847 | 0.009522 | 0.009715 | 0.009626 | 0.009626
[16 empty] | Specific volume (L/kgda) | 859.9499 | 859.9499 | 859.9499 | 819.8666 | 821.5285 | 839.8017 | 838.5182 | 852.7847 | 856.2503 | 854.6508 | 855.4816
[16 empty] | Enthalpy (J/gda) | 62.6948 | 62.6948 | 62.6948 | 34.5865 | 35.1772 | 41.6725 | 41.2163 | 47.6818 | 49.3109 | 48.559 | 48.8544
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
[15 empty] | AE345 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.197 | 12.78 | 19.1063 | 18.6471 | 23.3411 | 24.4553 | 23.9412 | 24.2323
[16 empty] | Humidity ratio (g/gda) | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.005155 | 0.005348 | 0.005259 | 0.005259
[16 empty] | Specific volume (L/kgda) | 850.423 | 850.423 | 850.423 | 814.1776 | 815.8412 | 833.8919 | 832.5816 | 846.8873 | 850.3306 | 848.7414 | 849.573
[16 empty] | Enthalpy (J/gda) | 36.4318 | 36.4318 | 36.4318 | 23.5615 | 24.1522 | 30.5618 | 30.0965 | 36.571 | 38.1911 | 37.4434 | 37.7387
[16 empty] | Mass flow rate (kgda/s) | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.73888 | 0.34102 | 0.39786 | n/a* | n/a* | 0.73888 | 0.73888
* n/a = not applicable
Last Hour of Simulation - Summary Outputs - Variable Air Volume System
|  | Zone 1 | Zone 1 | Zone 1 | Zone 2 | Zone 2 | Zone 2 | Pre-Heating | Cooling Coil |  |  |  | Zone 1 | Zone 2 | Last Hour of Simulation - Detailed Outputs - Variable Air Volume System
|  | Sensible | Sensible | Latent | Sensible | Sensible | Latent | Coil | Loads |  |  | Coil Outlet | Reheat Coil | Reheat Coil |  |  | Location
| Cases | Heating Load | Cooling Load | Load | Heating Load | Cooling Load | Load | Load | Sensible | Latent | Total | RH | Load | Load |  |  | Outdoor | Mixed | Preheat Coil | Cool Coil | Supply | Zone 1 | Zone 2 | Zone 1 | Zone 2 | Return Fan | Return Fan
|  | (QZH1sensible) | (QZC1sensible) | (QZ1latent) | (QZH2sensible) | (QZC2sensible) | (QZ2latent) | (QHpreheat) | (QCsensible) | (QClatent) | (QCtotal) | (RHcco) | (QH1reheat) | (QH2reheat) |  |  | Air | Air | Outlet | Outlet | Air | Supply Air | Supply Air | Air | Air | Inlet | Outlet
|  | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (kWh/h) | (%) | (kWh/h) | (kWh/h) | Cases | Variable | (oa) | (ma) | (pco) | (cco) | (sa) | (z1s) | (z2s) | (z1) | (z2) | (rfi) | (rfo)
| AE401 | 2.931 | 0 | 0.5861 | 2.345 | 0 | 0.8792 | 10.3477 | 0 | 0 | 0 | 4.1442 | 4.5023 | 4.8998 | AE401 | Dry bulb temperature (°C) | -29 | -28.9998 | 7.22 | 7.22 | 7.3069 | 46.7042 | 35.8918 | 21.1525 | 22.2626 | 21.8185 | 21.8618
| AE403 | 0 | 1.4663 | 0.5861 | 0 | 2.345 | 0.8792 | 0 | 1.4014 | 0 | 1.4014 | 55.0297 | 0 | 0 |  | Humidity ratio (g/gda) | 0.000259 | 0.000259 | 0.000259 | 0.000259 | 0.000259 | 0.000259 | 0.000259 | 0.002289 | 0.002287 | 0.002288 | 0.002288
| AE404 | 0 | 2.9318 | 0.5861 | 0 | 3.4963 | 0.8792 | 0 | 7.4077 | 6.256 | 13.6637 | 99.5745 | 0 | 0 |  | Specific volume (L/kgda) | 691.9367 | 691.9371 | 794.5864 | 794.5864 | 794.8327 | 906.4872 | 875.8442 | 836.7928 | 839.9471 | 838.6854 | 838.8085
| AE405 | 0 | 1.465 | 0.5861 | 0 | 2.3451 | 0.8792 | 0 | 4.1062 | 0 | 4.1062 | 52.8021 | 0 | 0 |  | Enthalpy (J/gda) | -28.5067 | -28.5067 | 7.9058 | 7.9058 | 7.9932 | 47.6002 | 36.7303 | 27.0684 | 28.1849 | 27.7383 | 27.782
| AE406 | 0 | 1.4667 | 0.5861 | 0 | 2.3451 | 0.8792 | 0 | 3.595 | 4.8345 | 8.4294 | 99.8734 | 0 | 0 |  | Mass flow rate (kgda/s) | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.28418 | 0.11367 | 0.17051 | n/a* | n/a* | 0.28418 | 0.28418
| AE426 | 0 | 1.4655 | 0.5861 | 0 | 2.3449 | 0.8792 | 0 | 3.5482 | 5.4007 | 8.9489 | 99.9259 | 0 | 0 | AE403 | Dry bulb temperature (°C) | 15.5 | 16.7936 | 16.7936 | 12.6648 | 12.7843 | 12.7842 | 12.7842 | 23.3287 | 24.4361 | 23.9837 | 24.0433
| AE445 | 0 | 1.4653 | 0.5861 | 0 | 2.3469 | 0.8792 | 0 | 4.1551 | 0 | 4.1551 | 49.4656 | 0 | 0 |  | Humidity ratio (g/gda) | 0.004684 | 0.004989 | 0.004989 | 0.004989 | 0.004989 | 0.004989 | 0.004989 | 0.006673 | 0.006735 | 0.006709 | 0.006709
[16 empty] | Specific volume (L/kgda) | 823.8699 | 827.966 | 827.966 | 816.1757 | 816.517 | 816.5156 | 816.5156 | 848.9007 | 852.1554 | 850.8257 | 850.9963
[16 empty] | Enthalpy (J/gda) | 27.4234 | 29.5088 | 29.5088 | 25.3217 | 25.4429 | 25.4407 | 25.4407 | 40.4191 | 41.703 | 41.1783 | 41.2389
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.3347 | 0.3347 | 0.3347 | 0.3347 | 0.1367 | 0.19782 | n/a* | n/a* | 0.33453 | 0.3347
[15 empty] | AE404 | Dry bulb temperature (°C) | 26.9 | 25.893 | 25.893 | 12.5034 | 12.8121 | 12.8113 | 12.8113 | 23.8848 | 25.1306 | 24.5564 | 24.7105
[16 empty] | Humidity ratio (g/gda) | 0.016767 | 0.013636 | 0.013636 | 0.00899 | 0.00899 | 0.00899 | 0.00899 | 0.009872 | 0.010221 | 0.010049 | 0.010049
[16 empty] | Specific volume (L/kgda) | 872.9227 | 865.7284 | 865.7284 | 820.9202 | 821.8072 | 821.805 | 821.805 | 854.822 | 858.8807 | 856.9949 | 857.4383
[16 empty] | Enthalpy (J/gda) | 69.8027 | 60.7786 | 60.7786 | 35.2565 | 35.5718 | 35.5712 | 35.5712 | 49.129 | 51.2912 | 50.2668 | 50.4245
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.53742 | 0.53742 | 0.53742 | 0.53742 | 0.2588 | 0.27862 | n/a* | n/a* | 0.53742 | 0.53742
[15 empty] | AE405 | Dry bulb temperature (°C) | 24.9 | 24.7705 | 24.7705 | 12.6606 | 12.78 | 12.78 | 12.78 | 23.3266 | 24.4337 | 23.982 | 24.0415
[16 empty] | Humidity ratio (g/gda) | 0.00448 | 0.004785 | 0.004785 | 0.004785 | 0.004785 | 0.004785 | 0.004785 | 0.006471 | 0.00653 | 0.006506 | 0.006506
[16 empty] | Specific volume (L/kgda) | 850.423 | 850.4668 | 850.4668 | 815.897 | 816.2379 | 816.2379 | 816.2379 | 848.6221 | 851.8707 | 850.5452 | 850.7156
[16 empty] | Enthalpy (J/gda) | 36.4318 | 37.0765 | 37.0765 | 24.8003 | 24.9213 | 24.9213 | 24.9213 | 39.9032 | 41.1785 | 40.6582 | 40.7188
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.33448 | 0.33448 | 0.33448 | 0.33448 | 0.13661 | 0.19788 | n/a* | n/a* | 0.33448 | 0.33448
[15 empty] | AE406 | Dry bulb temperature (°C) | 23 | 23.1492 | 23.1492 | 12.6651 | 12.7819 | 12.7795 | 12.7795 | 23.3282 | 24.435 | 23.9832 | 24.0414
[16 empty] | Humidity ratio (g/gda) | 0.015561 | 0.014881 | 0.014881 | 0.009115 | 0.009115 | 0.009115 | 0.009115 | 0.010812 | 0.010875 | 0.010849 | 0.010849
[16 empty] | Specific volume (L/kgda) | 859.9499 | 859.4653 | 859.4653 | 821.5475 | 821.8832 | 821.8767 | 821.8767 | 854.49 | 857.7638 | 856.4268 | 856.5945
[16 empty] | Enthalpy (J/gda) | 62.6948 | 61.1191 | 61.1191 | 35.7371 | 35.8564 | 35.8548 | 35.8548 | 50.9514 | 52.2437 | 51.7153 | 51.7749
[16 empty] | Mass flow rate (kgda/s) | 0.28418 | 0.3321 | 0.3321 | 0.3321 | 0.3321 | 0.13567 | 0.19629 | n/a* | n/a* | 0.33195 | 0.3321
[15 empty] | AE426 | Dry bulb temperature (°C) | 23 | 23 | 23 | 12.6651 | 12.7819 | 12.7819 | 12.7819 | 23.3274 | 24.4341 | 23.9816 | 24.0398
[16 empty] | Humidity ratio (g/gda) | 0.015561 | 0.015561 | 0.015561 | 0.00912 | 0.00912 | 0.00912 | 0.00912 | 0.010818 | 0.010878 | 0.010853 | 0.010853
[16 empty] | Specific volume (L/kgda) | 859.9499 | 859.9499 | 859.9499 | 821.5538 | 821.8896 | 821.8894 | 821.8894 | 854.4952 | 857.766 | 856.4281 | 856.5959
[16 empty] | Enthalpy (J/gda) | 62.6948 | 62.6948 | 62.6948 | 35.7494 | 35.8687 | 35.8687 | 35.8687 | 50.9648 | 52.2517 | 51.7248 | 51.7844
[16 empty] | Mass flow rate (kgda/s) | 0.33211 | 0.33211 | 0.33211 | 0.33211 | 0.33211 | 0.13558 | 0.19631 | n/a* | n/a* | 0.33189 | 0.33211
[15 empty] | AE445 | Dry bulb temperature (°C) | 24.9 | 24.9 | 24.9 | 12.6601 | 12.78 | 12.7799 | 12.7799 | 23.3271 | 24.4369 | 23.9858 | 24.0455
[16 empty] | Humidity ratio (g/gda) | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.00448 | 0.006163 | 0.006221 | 0.006196 | 0.006196
[16 empty] | Specific volume (L/kgda) | 850.423 | 850.423 | 850.423 | 815.499 | 815.8411 | 815.8409 | 815.8409 | 848.2073 | 851.4619 | 850.1374 | 850.3083
[16 empty] | Enthalpy (J/gda) | 36.4318 | 36.4318 | 36.4318 | 24.0307 | 24.1522 | 24.1521 | 24.1521 | 39.1194 | 40.3964 | 39.8745 | 39.9353
[16 empty] | Mass flow rate (kgda/s) | 0.33506 | 0.33506 | 0.33506 | 0.33506 | 0.33506 | 0.13671 | 0.19812 | n/a* | n/a* | 0.33483 | 0.33506
* n/a = not applicable